Outdoor Air-Cooled Liquid Chiller

HVAC Guide Specifications

Size Range: 80 to 500 Tons, Nominal

(265 to 1740 kW, Nominal)

Carrier Model Number: 30XA

- General

- SYSTEM DESCRIPTION

Microprocessor controlled, air-cooled liquid chiller for outdoor installation, utilizing screw compressors and low sound fans.

- QUALITY ASSURANCE

- Unit shall be rated in accordance with AHRI (Air-Conditioning, Heating, and Refrigeration Institute) Standard 550/590 (U.S.A.) latest edition and all units shall be ASHRAE (American Society of Heating, Refrigerating, and Air-Conditioning Engineers) 90.1 compliant.

- Unit construction shall comply with ASHRAE 15 Safety Code, UL (Underwriters Laboratories) 1995, and ASME (American Society of Mechanical Engineers) applicable codes (U.S.A. codes).

- The management system governing the manufacture of this product is ISO (International Organization for Standardization) 9001:2008 certified.

- Unit shall be full load run tested at the factory.

- DELIVERY, STORAGE AND HANDLING

- Unit controls shall be capable of withstanding 150°F (65.5°C) storage temperatures in the control compartment.

- Unit shall be stored and handled per unit manufacturer’s recommendations.

- Products

- EQUIPMENT

- General:

Factory assembled, single-piece chassis, air-cooled liquid chiller. Contained within the unit cabinet shall be all factory wiring, piping, controls, refrigerant charge (R-134a), and special features required prior to field start-up.

- Materials of Construction:

- The base rail is industrial-quality, 7 ga, zinc-dipped galvanized frame (with Magni-coated screws).

- Cabinet shall be galvanized steel casing with a baked enamel powder or pre-painted finish.

- Cabinet shall be capable of withstanding 500-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) (U.S.A.) B-117 standard.

- Fans:

- Condenser fans shall be direct-driven, 9-blade airfoil cross-section, reinforced polymer construction, shrouded-axial type, and shall be statically and dynamically balanced with inherent corrosion resistance.

- Air shall be discharged vertically upward.

- Fans shall be protected by coated steel wire safety guards.

- Compressor/Compressor Assembly:

- Comprised of semi-hermetic twin screw type compressors.

- Compressor motor shall be direct drive, 3500 rpm, protected by motor temperature sensors, suction gas cooled motor.

- Capacity control shall utilize an infinitely modulating slide valve to modulate capacity from 100% to 15% full load.

- Flooded Cooler:

- Shall be a mechanically cleanable tubes in a shell-and-tube type cooler with removable heads.

- Tubes shall be internally enhanced seamless-copper type rolled into tube sheets.

- Shall be equipped with Victaulic-type water connections.

- Shell and cooler heads shall be insulated with 3/4-in. PVC foam (closed-cell) with a maximum K factor of 0.28.

- Design shall incorporate 2 independent refrigerant circuits.

- Cooler shall be tested and stamped in accordance with ASME Code for a refrigerant working side pressure of 220 psig (1517 kPa). Cooler shall have a maximum water-side pressure of 300 psig (2068 kPa).

- Cooler shall have a cooler drain and vent.

- Low-ambient temperature protection: unit shall have factory-installed cooler heater (where applicable), and pumpout cycle to protect cooler from ambient temperature freeze down to 0°F (–17.8°C).

- Cooler shall be provided with a factory-installed flow switch.

- Condenser:

- Coil shall be air-cooled Novation® heat exchanger technology (MCHX) and shall have a series of flat tubes containing a series of multiple, parallel flow microchannels layered between the refrigerant manifolds. Novation coils shall consist of a two-pass arrangement. Coil construction shall consist of aluminum alloys for fins, tubes, and manifolds in combination with a corrosion-resistant coating.

- Tubes shall be cleaned, dehydrated, and sealed.

- Assembled condenser coils shall be pressure tested at the coil factory at 660 psig (5448 kPa) and subsequently shall be leak tested at 145 psig ±5 psig (1000 kPa ±34.5 kPa) and pressure tested at 350 psig (2413 kPa) at final unit assembly.

- To plan the chiller installation and for ease of maintenance/coil removal, all refrigerant piping entering and leaving the condenser coils shall be located on only one side of the chiller so the coils can be removed (when needed) from the side free of piping. This is important to consider because removing the coils from the header side, although possible, involves extra labor due to extra bending and brazing of the coil headers.

- Refrigeration Components:

Refrigerant circuit components shall include replaceable-core filter drier, moisture indicating sight glass, electronic expansion valve, discharge service valves and liquid line service valves, and complete operating charge of both refrigerant R-134a and compressor oil.

- Controls, Safeties, and Diagnostics:

- Unit controls shall include the following minimum components:

- Microprocessor with non-volatile memory. Battery backup system shall not be accepted.

- Separate terminal block for power and controls.

- Separate 115-v power supply to serve all controllers, relays, and control components.

- ON/OFF control switch.

- Replaceable solid-state controllers.

- Pressure sensors installed to measure suction, oil, economizer, and discharge pressure. Thermistors installed to measure cooler entering and leaving fluid temperatures and outside air temperature.

- Unit controls shall include the following functions:

- Automatic circuit lead/lag.

- Capacity control based on leaving chilled fluid temperature and compensated by rate of change of return-fluid temperature with temperature set point accuracy to 0.1°F (0.05°C).

- Limiting the chilled fluid temperature pull-down rate at start-up to an adjustable range of 0.2°F to 2°F (0.1 to 1.1°C) per minute to prevent excessive demand spikes at start-up.

- Seven-day time schedule.

- Leaving chilled fluid temperature reset from return fluid and outside air temperature.

- Chilled water pump start/stop control.

- Chiller control for parallel chiller applications without addition of hardware modules and control panels (requires thermistors).

- Timed maintenance scheduling to signal maintenance activities for strainer maintenance and user-defined maintenance activities.

- Low ambient protection to energize cooler heaters (if installed).

- Single step demand limit control activated by remote contact closure.

- Periodic pump start to ensure pump seals are properly maintained during off-season periods.

- Night time sound mode to reduce the sound of the machine by a user-defined schedule.

- Diagnostics:

- The control panel shall include, as standard, a display:

- Touch screen display consisting of 1/4 VGA LCD (liquid crystal display) with adjustable contrast and backlighting.

- Display shall allow a user to navigate through menus, select desired options and modify data.

- Features of the display shall include:

- Display shall be customizable and allow up to 72 data points.

- Display shall support both local equipment or network made for remote mount.

- Display shall allow access to configuration, maintenance, service, set point, time schedules, alarm history and status data.

- Display shall have one button for chiller on/off.

- Display shall include three levels of password protection against unauthorized access to configuration and maintenance information, and display set up parameters.

- Display shall allow for easy connection of a portable hand held technician tool to access information and upload and/or download chiller settings.

- Display shall be compatible with the Carrier Comfort Network® (CCN) system and provide network alarm acknowledgment or indication and provide capability to fully monitor and control chiller.

- Display alarms and parameters shall be capable of being displayed in full text.

- Display shall be capable of displaying the last 50 alarms and will store a snapshot of a minimum of 20 status data parameters for each alarm.

- Compressor run hours.

- Compressor number of starts.

- Compressor current.

- Time of day:

- Display module, in conjunction with the microprocessor, must also be capable of displaying the output (results) of a service test. Service test shall verify operation of every switch, thermistor, fan, and compressor before chiller is started.

- Diagnostics shall include the ability to review a list of the 30 most recent alarms with clear language descriptions of the alarm event. Display of alarm codes without the ability for clear language descriptions shall be prohibited.

- An alarm history buffer shall allow the user to store no less than 30 alarm events with clear language descriptions, time and date stamp event entry.

- The chiller controller shall include multiple connection ports for communicating with the local equipment network, the Carrier Comfort Network® (CCN) system and the ability to access all chiller control functions from any point on the chiller.

- The control system shall allow software upgrade without the need for new hardware modules.

- Safeties:

- Unit shall be equipped with thermistors and all necessary components in conjunction with the control system to provide the unit with the following protections:

- Loss of refrigerant charge.

- Reverse rotation.

- Low chilled fluid temperature.

- Motor overtemperature.

- High pressure.

- Electrical overload.

- Loss of phase.

- Loss of chilled water flow.

- Condenser-fan motors shall have internal overcurrent protection.

- Operating Characteristics:

- Unit shall be capable of starting and running at outdoor ambient temperatures from 32°F (0°C) to 125.6°F (52°C) for all sizes.

- Unit shall be capable of starting up with 95°F (35°C) entering fluid temperature to the cooler.

- Motors:

Condenser-fan motors shall be totally enclosed, air over, single speed, 3-phase type with permanently lubricated bearings and Class F insulation.

- Electrical Requirements:

- Unit primary electrical power supply shall enter the unit at a single location (all chiller voltage/size combinations shall have the ability to accommodate 2 power supplies to meet job-specific requirements).

- Primary electrical power supply shall be rated to operate up to 131°F (55°C) for 401-501 units and up to 125°F (52°C) ambient temperature for all other models.

- Unit shall operate on 3-phase power at the voltage shown in the equipment schedule.

- Control points shall be accessed through terminal block.

- Unit shall be shipped with factory control and power wiring installed.

- Chilled Water Circuit:

- Chilled water circuit shall be rated for 300 psig (2068 kPa). Units with optional pump package are rated for 150 psig (1034 kPa) working pressure.

- Thermal dispersion proof of flow switch shall be factory installed and wired.

- Optional hydronic package:

- With or without VFD (variable frequency drive) (30XA090-162 units only, not available with high SCCR [short circuit current rating]):

- Field pipe connections shall be Victaulic type.

- Optional single or primary/stand-by operation pump systems. Dual pump systems shall have a pump discharge check valve.

- Pumps shall be vertical in-line, single stage design, and capable of being serviced without disturbing piping connections.

- Pump casing shall be of class 30 cast iron.

- The impeller shall be of cast bronze, closed type, dynamically balanced, keyed to the shaft and secured by locking cap screw.

- The hydronic kit will be provided with a flush line connection to ensure lubrication at the seal face and allow for positive venting of the seal chamber.

- Each port shall be fitted with an isolation valve that allow the units to operate in parallel or standby, yet may be used to isolate one pumping unit for servicing or removal with the other pump still running.

- Pump shall be rated for 150 psig (1034 kPa) working pressure.

- The pump case shall have gage tappings at the suction and discharge nozzles and include drain ports.

- Dual pumps shall allow for the servicing of one pump without draining the chilled water loop.

- Motors shall be premium efficiency, Totally Enclosed Fan Cooled (TEFC) 3-phase type with grease lubricated ball bearings.

- Each pump shall be factory tested per Hydraulic Institute Standards.

- Pressure/temperature taps (3) shall be factory installed to measure the pressure differential across the pump and across the strainer.

- Combination valve (which includes check, isolation, and modulation) shall be factory installed. Pressure/temperature taps (2) shall be factory installed to measure the pressure differential across the combination valve.

- Hydronic assembly shall have factory-supplied electric freeze protection to –20°F (–29°C).

- Piping shall be Schedule 40 black steel.

- Cast iron or ductile iron body 1/8 in. perforated strainer. A factory-installed, removable fine mesh start-up strainer for initial run period shall be included. The start-up strainer must be removed within 24 hours after chiller start-up.

- With VFD (these comments are applicable in addition to the comments in section a when the VFD hydronic package is employed [30XA090-162 units only]):

- The drive shall be of the voltage vector control - pulse with modulation (VVC-PWM) type, providing near unity displacement power factor without the need for external power factor correction capacitors at all loads and speeds.

- The drive and motor protection shall include: motor phase to ground fault, loss of supply phase, over voltage, under voltage, motor over temperature, inverter overload, over current. Over current is not allowed, ensuring hydronic units will not overload the motor at any point in the operating range of the unit.

- Sensorless control software shall be available in the hydronic unit to provide automatic speed control without the need for pump mounted (internal/external) or remotely mounted differential pressure system feedback sensors. Control mode setting and minimum/maximum head set points shall be set at the factory and be user adjustable via the programming interface.

- The integrated control shall incorporate an integrated graphical user interface that shall provide running and diagnostic information and identify faults and status in clear English language. Faults shall be logged/recorded for review at a later date. It shall be possible to upload parameters from one drive into the non-volatile memory of a computer and download the parameters into other drives requiring the same settings. The key pad shall incorporate Hand-Off-Auto pushbuttons to enable switching between BMS (building management systems) and manual control. The drive shall incorporate a USB port for direct connection to a PC and an RS485 connection with Modbus RTU protocol. Optional protocols available should include BACnet and LonWorks.

- The control shall have the following additional features: Sensorless override for BMS, manual pump control or closed loop PID control; programmable skip frequencies and adjustable switching frequency for noise/vibration control; auto alarm reset; motor pre-heat function; six programmable digital inputs; two analog inputs; one programmable analog/digital output; two volt-free contacts.

- The hydronic unit shall be capable of operating in any of the following control modes:

- Duty pump and standby pumps with sensorless control.

- Duty pump and standby pumps with remote sensor or building system (BAS) control.

- Special Features:

Certain standard features are not applicable when the features designated by * are specified. For assistance in amending the specifications, contact your Carrier representative.

- DX (Direct Expansion) Cooler Option (Not Available on sizes 401-501):

- Shell-and-tube type, direct expansion.

- Tubes shall be internally enhanced seamless-copper type rolled into tube sheets.

- Shall be equipped with Victaulic-type water connections.

- Shell shall be insulated with 3/4-in. (19 mm) PVC foam (closed-cell) with a maximum K factor of 0.28.

- Design shall incorporate a minimum of 2 independent direct-expansion refrigerant circuits.

- Cooler shall be rested and stamped in accordance with ASME Code for a refrigerant working side pressure of 220 psig (1517 kPa). Cooler shall have a maximum water-side pressure of 300 psig (2068 kPa).

- Cooler shall be provided with a factory-installed flow switch.

- Low Ambient Temperature Head Pressure Control:

Unit shall be capable of running at outdoor ambient temperatures down to –20°F (–29°C) with the addition of antifreeze in the cooler circuit, wind baffles, and field-installed or factory-installed solid-state low ambient temperature head pressure control with condenser coil temperature sensor.

- Unit-Mounted Non-Fused Disconnect:

Unit shall be supplied with factory-installed, lockable, non-fused electrical disconnect for main power supply. This is not available with the combination of dual point power and high SCCR (short circuit current rating).

- Optional Condenser Coil Materials:

- E-coated microchannel coils:

E-coated aluminum microchannel coil shall have a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins or louvers. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. E-coat shall have a thickness of 0.8 to 1.2 mil with top coat having a uniform dry film thickness from 1.0 to 2.0 mil on all external coil surface areas including fin edges. E-coated coils shall have superior hardness characteristics of 2H per ASTM D3363-00 and cross hatch adhesion of 4B-5B per ASTM D3359-02. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). E-coated coil shall have superior impact resistance with no cracking, chipping, or peeling per NSF/ANSI 51-2002 Method 10.2. E-coated aluminum microchannel coils shall be capable of withstanding an 8000-hour salt spray test in accordance with the ASTM (American Society for Testing and Materials) (U.S.A.) B-117 Standard.

- Aluminum fin/copper-tube coils:

Coil shall be constructed of seamless copper tubes mechanically bonded to aluminum fins. Fins shall have wavy enhancements. These condenser coils are recommended with remote cooler applications. These coils are not recommended for corrosive environments.

- Pre-coated aluminum-fin coils:

Shall have a durable epoxy-phenolic coating to provide protection in mildly corrosive coastal environments. Coating shall be applied to the aluminum fin stock prior to the fin stamping process to create an inert barrier between the aluminum fin and copper tube. Epoxy-phenolic barrier shall minimize galvanic action between dissimilar metals.

- Copper-fin coils:

Shall be constructed of copper fins mechanically bonded to copper tubes and copper tube sheets. Galvanized steel tube sheets shall not be acceptable. A polymer strip shall prevent coil assembly from contacting sheet metal coil pan to minimize potential for galvanic corrosion between the coil and pan. All copper construction shall provide protection in moderate coastal applications.

- E-coated aluminum-fin coils:

Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins. Coating process shall ensure complete coil encapsulation. Color shall be high gloss black with gloss — 60° of 65-90% per ASTM D523-89. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges. Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion of 4B-5B per ASTM D3359-93. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). Corrosion durability shall be confirmed through testing to no less than 3000 hours salt spray per ASTM B117-90. Coil construction shall be aluminum fins mechanically bonded to copper tubes.

- E-coated copper-fin coils:

Shall have a flexible epoxy polymer coating uniformly applied to all coil surface areas without material bridging between fins. Coating process shall ensure complete coil encapsulation. Color shall be high gloss black with gloss — 60° of 65-90% per ASTM D523-89. Uniform dry film thickness from 0.8 to 1.2 mil on all surface areas including fin edges. Superior hardness characteristics of 2H per ASTM D3363-92A and cross hatch adhesion of 4B-5B per ASTM D3359-93. Impact resistance shall be up to 160 in./lb (ASTM D2794-93). Humidity and water immersion resistance shall be up to minimum 1000 and 250 hours respectively (ASTM D2247-92 and ASTM D870-92). Corrosion durability shall be confirmed through testing to no less than 3000 hours salt spray per ASTM B117-90. Coil construction shall be copper-fins mechanically bonded to copper tube sheets. Galvanized steel tube sheets shall not be acceptable. A polymer strip shall prevent coil assembly from contacting sheet metal coil pan to maintain coating integrity and minimize corrosion potential between the coil and pan.

- Remote Enhanced Display:

Unit shall be supplied with indoor-mounted, remote, 40-character per line, 16-line display panel for field installation.

- Chillervisor System Manager III Multi-Unit Control:

Field-installed control shall sequence 2 chillers in series, or between 2 and 8 chillers in parallel in a single system.

- Energy Management Module:

A factory or field-installed module shall provide the following energy management capabilities: 4 to 20 mA signals for leaving fluid temperature reset, cooling set point reset or demand limit control; 2-step demand limit control (from 0% to 100%) activated by a remote contact closure; and discrete input for “Ice Done” indication for ice storage system interface.

- Condenser Coil Trim Panels:

Unit shall be supplied with field-installed coil covers.

- BACnet Communication Option:

Shall provide pre-programmed factory-installed communication capability with a BACnet MS/TP network. Allows integration with i-Vu® Open control system or a third-party BACnet building automation system. No field programming shall be required.

- BACnet/Modbus Translator Control:

Unit shall be supplied with factory or field-installed interface between the chiller and a BACnet Local Area Network (LAN, i.e., MS/TP EIA-485). Field programming shall be required.

- LON Translator Control:

Unit shall be supplied with factory or field-installed interface between the chiller and a Local Operating Network (LON; i.e., LonWorks FT-10A ANSI/EIA-709.1). Field programming shall be required.

- Navigator™ hand-held portable display:

- Portable hand-held display module with a minimum of 4 lines and 20 characters per line, or clear English, Spanish, Portuguese or French language.

- Display menus shall provide clear language descriptions of all menu items, operating modes, configuration points and alarm diagnostics. Reference to factory codes shall not be accepted.

- RJ-14 connection plug shall allow display module to be connected to factory-installed receptacle.

- Industrial grade coiled extension cord shall allow the display module to be moved around the chiller.

- Magnets shall hold the display module to any sheet metal panel to allow hands-free operation.

- Display module shall have NEMA 4x housing suitable for use in outdoor environments.

- Display shall have backlight and contrast adjustment for easy viewing in bright sunlight or night conditions.

- Raised surface buttons with positive tactile response.

- Touch Pilot™ Display:

Unit shall be supplied with a field-installed, remote-mount, touch screen display for network attachment to the chiller. The Touch Pilot display provides information in clear English, Spanish, Portuguese, or French language.

- Isolation Valve Option:

Unit shall be supplied with factory-installed isolation valve which provides a means of isolating the compressors from the cooler vessel, which is beneficial in servicing the chiller. The isolation option comes in various configurations depending on the cooler type (flooded or DX) and the installation region (Middle Eastern or elsewhere). On all units equipped with the flooded cooler which are not installed in the Middle East region, a liquid line service valve and a motorized discharge isolation valve are always provided per refrigerant circuit. For Middle Eastern regions only, a manual discharge valve is standard and a motorized discharge ball valve is optional. On units equipped with the optional DX cooler, the liquid line service valve and a manual discharge service valve is included in the isolation valve option, regardless of the region of installation. Regardless of which cooler option is employed, the selection of the isolation valve option results in chillers which are equipped with a liquid line service valve, a discharge service valve (motorized or manual type), and a series of valves on or near the cooler. The net effect is to provide isolation capability in the condenser area, the cooler area and the compressor area.

NOTE: The only situation in which the isolation of the condenser area allows the full charge to be stored in the condenser is when round tube, plate fin (RTPF) coils are employed.

- Suction Line Insulation:

Unit shall be supplied with suction line insulation. Insulation shall be tubular closed-cell insulation. This option shall be required with applications with leaving fluid temperatures below 30°F (–1.1°C) and recommended for areas of high dewpoints where condensation may be a concern.

- Service Option:

Unit shall be provided with a service option which provides a remote service port for Navigator™ connection and a factory-installed convenience outlet that includes 4-amp GFI (ground fault interrupt) receptacle with independent fuse protection. Convenience outlet shall be 115-v female receptacle. Service option not available with 380 v.

- Remote Service Port:

Shall be a field-installed receptacle for Navigator device connection.

- Wye-Delta Starter:

Unit shall have a factory-installed, wye-delta start to minimize electrical inrush current.

- Control Transformer:

Unit shall be supplied with a factory-installed transformer that will allow supply control circuit power from the main unit power supply.

- GFI Convenience Outlet:

Shall be factory or field-installed and mounted with easily accessible 115-v female receptacle. Shall include 4 amp GFI (ground fault interrupt) receptacle. Not available with 380-v units.

- Plus-One-Pass Cooler (Flooded Coolers Only):

Unit shall be equipped with plus-one-pass cooler heads to be used with high delta T application. This option is not available on unit sizes 401-501.

- Minus-One-Pass Cooler (Flooded Coolers Only):

Unit shall be equipped with minus-one-pass cooler heads with reduced water-side pressure drop for series flow dual chiller control or high chilled water flow applications.

- High Ambient Temperature:

Unit shall be equipped with high speed condenser fan motors to improve performance at high ambient temperatures. This option shall be required for 30XA401-501 chillers, and it is also required for all 30XA401-501 chillers which are operating in multi-chiller configurations or have ambient temperatures at or above 100°F (37.8°C).

- Security Grilles:

Unit shall be provided with factory (or field) installed painted grilles to protect the condenser, cooler and compressor.

- Upper Hail Guard:

Unit shall be equipped with a factory-installed option consisting of louvered panels on the ends of the machine which firmly fasten to the machine frame. These panels shall cover the unit from the top to the bottom of the coils, thus providing protection of the coils from hail damage.

- Full Hail Guard:

Unit shall be equipped with field-installed accessory consisting of hinged, louvered panels, which cover both ends of the unit. This accessory provides complete protection from hail.

- Full End Screen:

Unit shall be equipped with a factory-installed option consisting of louvered panels that cover the machine ends from top to bottom and firmly fasten to the machine frame. These end screens function as a privacy screen and also provide hail protection.

- Low Sound Package:

Unit shall be provided with sound attenuation package to include sheet metal enclosures with sound absorbing panels for each co-mpressor.

- Remote Cooler Kit:

Allows remote installation of the cooler. This is not available on sizes 401-501.

- Minimum Load Control:

Unit shall be equipped with microprocessor- controlled minimum load control that shall permit unit operation below the minimum standard operation (varies by unit size).

- High SCCR (Short Circuit Current Rating):

The optional high SCCR (short circuit current rating) device shall allow the chiller to tolerate a 65 kA (460-v units) or 25 kA (575-v units) short circuit current for a brief period of time while protecting downstream components. The high SCCR option shall provide a higher level of protection than the standard unit. This option is only available on 30XA140-352 and only at 460 or 575 volts.

- Dual Chiller Accessory Kit:

For dual chiller applications (with units piped in parallel), unit shall be provided with the additional hardware (thermistors, wells, connectors) required for proper system operation.

- Seismic Certification:

A seismic kit is available which will result in a unit SDS (seismic design acceleration parameter) level of 2.4.

# Footnotes

Modbus is a registered trademark of Schneider Electric.

BACnet is a registered trademark of ASHRAE (American Society of Heating, Refrigerating, and Air-Conditioning Engineers).

LonWorks is a registered trademark of Echelon Corporation.